## LSN50v2-8-M16
Template for MSB1.x / ecoBolt configuration
Use one row per device
Explanation can be found on the tab / sheet "Config"
DevEUI | Gateway IP | Steam Trap Type | Mounting Type | Model | DN | Differential Pressure [barg] | Application | Condensate Load
A84041119184FFF0 | 192.168.23.1 | membrane | RFC | MSB1.0 | 15 | 32 | Steam tracer | low
A84041119184FFF1 | 192.168.23.1 | membrane | ADP | MSB1.2 | 40 | 15 | Steam tracer | mid
A84041134184FF58 | 192.168.23.1 | ball float | PBS | MSB1.2 | 50 | 2 | Steam line | mid
A84041134184FF59 | 192.168.24.1 | bimetallic | ADP | MSB1.2 | 50 | 7 | Steam line | low
A8404113F184FFC4 | 192.168.24.1 | ball float | RFC | MSB1.0 | 65 | 19 | Heat exchanger | mid
A8404113F184FFC5 | 192.168.178.1 | ball float | RFC | MSB1.0 | 25 | 22 | Heat exchanger | high

## Explanation
Default Gateway Credentials
default username | apiuser
default password | password
DevEUI | 64-bit globally-unique Extended Unique Identifier (can be found on the name plate).
Gateway IP | Needs to be changed according to the gateway settings (IPv4).
Steam Trap Type | Description
bimetallic | Thermostatic steam trap (bimetallic, e.g. BK45, SMC32)
membrane | Thermostatic steam trap (membrane, capsule and balanced pressure, e.g. MK45, BPC32)
ball float | Mechanical steam trap (ball float, e.g. UNA45, FT57)
Mounting type | Description
PBS | Pressure-bearing screw
ADP | Pressure-bearing screw and 90° adapter
RFC | Retrofit clamp / clip
MSB | Description
MSB1.0 | Amplifier with high gain for low pressures
MSB1.2 | Amplifier with low gain for high pressures
DN | Description
15 | 1/2"
20 | 3/4"
25 | 1"
40 | 1 1/2"
50 | 2"
65 | 2 1/2"
Differential Pressure [barg] | Description
0 | Minimum value
32 | Maximum value
Application | Description
Steam tracer | usually low condensate loads
Steam line | usually low condensate loads
Heat exchanger | usually high condensate loads
Condensate load | Description
low | < 20 kg/h
mid | 20 - 100 kg/h
high | > 100 kg/h