## Config
Template for MSB1.x / ecoBolt configuration
2023-09-22
Use one row per device
Explanation can be found on the tab / sheet "Description"
The orange columns are calculated automatically
A red cell means the config is not set correctly (e.g. too high pressure)
DevEUI | Server | Steam Trap Type | DN | Mounting Type | Differential Pressure [barg] | Hardware Model | Application | Condensate Load | twkup [s] | Defective Alarm [d] | ErrCntTHDef | Defective Warning [d] | WarnCntTHDef
A84041119184FFF0 | 192.168.23.1 | bimetallic | 15 | PBS | 22 | MSB1.0 | Steam tracer | low | 3600 | 30 | 720 | 15 | 360
A84041119184FFF1 | 192.168.23.1 | membrane | 20 | RFC | 10 | MSB1.0 | Steam line | low | 3600 | 30 | 720 | 15 | 360
A84041134184FF58 | 192.168.23.1 | ball-float | 25 | PBS | 2 | MSB1.0 | Steam tracer | low | 3600 | 10 | 240 | 5 | 120
A84041134184FF59 | 192.168.24.1 | bimetallic | 40 | RFC | 1 | MSB1.0 | Steam tracer | low | 3600 | 10 | 240 | 5 | 120
A8404113F184FFC4 | 192.168.24.1 | ball-float | 50 | ADP | 15 | MSB1.2 | Heat exchanger | high | 3600 | 3 | 72 | 1.5 | 36
A8404113F184FFC5 | 192.168.178.1 | bimetallic | 65 | RFC | 23 | MSB1.0 | Heat exchanger | high | 3600 | 3 | 72 | 1.5 | 36
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0
MSB1.0

## Description
Default Gateway Credentials
default username | apiuser
default password | password
DevEUI | 64-bit globally-unique Extended Unique Identifier. Can be found on the name plate.
Gateway IP | Needs to be changed according to the gateway settings.
Steam Trap Type | Description
bimetallic | Thermostatic steam trap (bimetallic, e.g. BK45, SMC32)
membrane | Thermostatic steam trap (membrane, capsule and balanced pressure, e.g. MK45, BPC32)
ball-float | Mechanical steam trap (ball float, e.g. UNA45, FT57)
DN | Description
15 | 1/2"
20 | 3/4"
25 | 1"
40 | 1 1/2"
50 | 2"
65 | 2 1/2"
Mounting type | Description
PBS | Pressure-bearing screw
ADP | Pressure-bearing screw and 90° adapter
RFC | Retrofit clamp / clip
Differential Pressure [barg] | Description
0 | Minimum value
32 | Maximum value
Model | Description
MSB1.0 | Amplifier with high gain for low pressures (set automatically by the excel sheet)
MSB1.2 | Amplifier with low gain for high pressures (set automatically by the excel sheet)
Application | Description
Steam tracer | usually low condensate loads
Steam line | usually low condensate loads
Heat exchanger | usually high condensate loads
Condensate load | Description
low | <20kg/h (defective steam traps are detected earlier)
mid | 20…100kg/h
high | >100kg/h (defective steam traps are detected later)
twkup [s] | Description
149 | Minimum value (1:29min)
86400 | Maximum value (1 day)
Defective Alarm [d] | Description
1 | Minimum value to output a defective alarm, State Alarm Bit 7
100 | Maximum value to output a defective alarm, State Alarm Bit 7
ErrCntTHDef | Description
x | Only used as informative column (necessary for LoRa downlink)
Defective Warning [d] | Description
1 | Minimum value to output a defective warning, State Alarm Bit 3
100 | Maximum value to output a defective warning, State Alarm Bit 3
WarnCntTHDef | Description
x | Only used as informative column (necessary for LoRa downlink)
Excel PW:
connected-services